## Water Import Concept A
Evaporation Losses from Canal
Canal width | 30 | ft
Canal apex elevation | 305 | ft
Canal depth | 12 | ft
Canal exposed length | 150 | miles
Canal exposed length | 792000 | ft
Canal capacity | 54000 | AF
Avg Annual Precipitation Inflow Rate | 7.5 | AF/yr
Avg Annual Evaporation Rate | 68 | in/yr
Net Avg Annual Canal Balance | -25492.5 | AF/yr
Avg Daily Flow Rate | -78.4385 | AF/day
constant | 325851 | gal/AF
Flow Rate (gpm) | -17749.48 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | -1.1198 | cu-m/s
Sea Water Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Head Pressure | 305 | ft
Head Pressure | 92.964 | m
Archimedes Screw Turbine Efficiency | 85%
Power from Water | -885126.168 | Watts
Peak Flow Rate | -1.1198 | cu-m/s
Hours per day | 24 | hr
Daily Flow Rate | -78.4385 | AF/day
System Availability | 0.95
Power Sales Rate | 0.1 | $/kWh
Revenue loss while evaporating | -88.5126 | $/hr
Annual Hydro Power Evaporation Loss | -736601.997 | $/yr
Pump Up Calculation
Pump head needed for canal drop | 204.855 | feet
Daily Seawater Pump Up Rate | 2800 | AF/day
Seawater Salinity Sea of Cortez | 37000 | ppm TDS
Annual Seawater Pump Up Rate | 910000 | AF/yr
constant | 325851 | gal/AF
Pumping Hours per day | 24 | hr
Pump Up Flow Rate | 633599.1667 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | 39.9742 | cu-m/s
Seawater Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Pump Head | 509.855 | ft
Pump Head | 155.4038 | m
Archimedes Screw Pump Efficiency | 85% | %
Generator Efficiency | 92%
Gearbox Efficiency | 97%
Net Efficiency | 75.85%
Power to Lift Water | 81918798.7265 | Watts
Power to Lift Water | 81.9188 | MW
Pump Up Power Rate | 0.1 | $/kWh
Cost to Lift Water | 8191.8799 | $/hr
Annual Power Cost to Lift Seawater | 71760867.6844 | $/yr
Energy Recovery Calculation
Drop subtracted for canal flow | 83.055 | ft
Annual Hydro Recovery Rate | 884507.5 | AF/yr
Avg Daily Hydro Recovery Rate | 2721.5615 | AF/day | 993369.9615
constant | 325853.3837 | gal/AF
Canal Flow Rate (gpm) | 615854.1918 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | 38.8544 | cu-m/s
Seawater Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Head Pressure | 460.445 | ft
Head Pressure | 140.3436 | m
Archimedes Screw Turbine Efficiency | 85%
Generator Efficiency | 92%
Gearbox Efficiency | 97%
Net Efficiency | 75.85%
Power from Water | 41374404.4806 | Watts
Power from Water | 41.3744 | MW
Peak Flow Rate | 34.6736 | cu-m/s
Operating Hours per day | 24 | hr
Daily Flow Rate | 2428.7215 | AF/day
System Availability | 95%
Power Rate | 0.085 | $/kWh
Revenue while running | 3516.8244 | $/hr
Annual Hydro Recovery Revenue | 29267012.4974 | $/yr
Net Power Output | -40.5444 | MW
Cost and Revenue Calculation
Unit Cost of Turbine Generators | 2400 | $/kW
Capital Cost of Turbine Generators | 99298570.7534 | $
Life of Turbine Generators | 25 | yrs
O&M Cost of Turbine Generators | 100 | $/kW
Amortized Cost of Turbine Generators | 3972042.8301 | $/yr
Cost of Spillways | 1000 | $/kW
Capital Cost of Spillways | 41374404.4806 | $
Life of Spillways | 50 | yrs
O&M Cost of Spillways | 3 | $/kW
Amortized Cost of Spillways | 827491.0896 | $/yr
Cost of Power Transmission | 1.69 | $/kW-month
Cost of Power Transmission | 0.0023472 | $/kWh
Annual Cost of Power Transmission | 839072.9229 | $/yr
Unit Cost of Pump Screws | 2400 | $/kW
Capital Cost of Pump Screws | 196605116.9436 | $
Life of Pump Screws | 25 | yrs
O&M Cost of Pump Screws | 100 | $/kW
Amortized Cost of Pump Screws | 7864304.6777 | $/yr
Unit Cost of Seawater Pump Motors | 1000 | $/kGPM
Capital Cost of Seawater Pump Motors | 615854.1918 | $
Life of Seawater Pump Motor | 15 | yrs
O&M Cost of Seawater Pump Motors | 100 | $/kGPM
Amortized Cost of Seawater Pump Motors | 41156.9461 | $/yr
Total Annual Cost | 13544068.4665 | $/yr
Net Revenue less cost | -56774525.6505 | $/yr
Total Capital Cost (pumps,turbines 2013) | 337893946.3695
Total Capital Cost (pumps,turbines 2021) | 395335917.2523

## Water Import Concept B
Evaporation Losses from Canal
Canal width | 30 | ft
Canal apex elevation | 40 | ft
Canal depth | 12 | ft
Canal exposed length | 175.79 | miles
Canal exposed length | 928171.2 | ft
Canal capacity | 63284.4 | AF
Avg Annual Precipitation Inflow Rate | 7.5 | AF/yr
Avg Annual Evaporation Rate | 68 | in/yr
Net Avg Annual Canal Balance | -29876.8 | AF/yr
Avg Daily Flow Rate | -91.9286 | AF/day
constant | 325851 | gal/AF
Flow Rate (gpm) | -20802.105 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | -1.3124 | cu-m/s
Sea Water Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Head Pressure | 40 | ft
Head Pressure | 12.192 | m
Archimedes Screw Turbine Efficiency | 85%
Power from Water | -136046.3781 | Watts
Peak Flow Rate | -1.3124 | cu-m/s
Hours per day | 24 | hr
Daily Flow Rate | -91.9286 | AF/day
System Availability | 0.95
Power Sales Rate | 0.1 | $/kWh
Revenue loss while evaporating | -13.6046 | $/hr
Annual Hydro Power Evaporation Loss | -113217.7959 | $/yr
Pump Up Calculation
Pump head needed for canal drop | 263.685 | feet
Daily Seawater Pump Up Rate | 2800 | AF/day
Seawater Salinity Sea of Cortez | 37000 | ppm TDS
Annual Seawater Pump Up Rate | 910000 | AF/yr
constant | 325851 | gal/AF
Pumping Hours per day | 24 | hr
Pump Up Flow Rate | 633599.1667 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | 39.9742 | cu-m/s
Seawater Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Pump Head | 303.685 | ft
Pump Head | 92.5632 | m
Archimedes Screw Pump Efficiency | 85% | %
Generator Efficiency | 92%
Gearbox Efficiency | 97%
Net Efficiency | 75.85%
Power to Lift Water | 48793304.746 | Watts
Power to Lift Water | 48.7933 | MW
Pump Up Power Rate | 0.1 | $/kWh
Cost to Lift Water | 4879.3305 | $/hr
Annual Power Cost to Lift Seawater | 42742934.9575 | $/yr
Energy Recovery Calculation
Drop subtracted for canal flow | 0 | ft
Annual Hydro Recovery Rate | 0 | AF/yr
Avg Daily Hydro Recovery Rate | 0 | AF/day | 0
constant | 325853.3837 | gal/AF
Canal Flow Rate (gpm) | 0 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | 0 | cu-m/s
Seawater Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Head Pressure | 278.5 | ft
Head Pressure | 84.8868 | m
Archimedes Screw Turbine Efficiency | 85%
Generator Efficiency | 92%
Gearbox Efficiency | 97%
Net Efficiency | 75.85%
Power from Water | 0 | Watts
Power from Water | 0 | MW
Peak Flow Rate | 0 | cu-m/s
Operating Hours per day | 24 | hr
Daily Flow Rate | 0 | AF/day
System Availability | 95%
Power Rate | 0.085 | $/kWh
Revenue while running | 0 | $/hr
Annual Hydro Recovery Revenue | 0 | $/yr
Net Power Output | -48.7933 | MW
Cost and Revenue Calculation
Unit Cost of Turbine Generators | 2400 | $/kW
Capital Cost of Turbine Generators | 0 | $
Life of Turbine Generators | 25 | yrs
O&M Cost of Turbine Generators | 100 | $/kW
Amortized Cost of Turbine Generators | 100 | $/yr
Cost of Spillways | 1000 | $/kW
Capital Cost of Spillways | 0 | $
Life of Spillways | 50 | yrs
O&M Cost of Spillways | 0 | $/kW
Amortized Cost of Spillways | 0 | $/yr
Cost of Power Transmission | 1.69 | $/kW-month
Cost of Power Transmission | 0.0023472 | $/kWh
Annual Cost of Power Transmission | 0 | $/yr
Unit Cost of Pump Screws | 2400 | $/kW
Capital Cost of Pump Screws | 117103931.3903 | $
Life of Pump Screws | 25 | yrs
O&M Cost of Pump Screws | 100 | $/kW
Amortized Cost of Pump Screws | 4684257.2556 | $/yr
Unit Cost of Seawater Pump Motors | 1000 | $/kGPM
Capital Cost of Seawater Pump Motors | 633599.1667 | $
Life of Seawater Pump Motor | 15 | yrs
O&M Cost of Seawater Pump Motors | 100 | $/kGPM
Amortized Cost of Seawater Pump Motors | 42339.9444 | $/yr
Total Annual Cost | 4726697.2001 | $/yr
Net Revenue less cost | -47582849.9534 | $/yr
Total Capital Cost (pumps 2013) | 117737530.557
Total Capital Cost (pumps 2021) | 137752910.7517